## Orders
Municipality Name | DWS # | DWS Category | DWS Name | Owner Legal Name | Operating Authority Legal Name | Order Summary | Order Type | Instrument Status | Director's Order | Date Instrument Issued | Fiscal Year
Oliver Paipoonge | 260016848 | SNMNRS | Options Northwest Group Home Well Supply | Options Northwest Personal Support Services | Options Northwest Personal Support Services | This order required the owner of the drinking water system to: ensure an engineering evaluation report is prepared by a licensed practitioner and that once the report is prepared, that the owner operate the system in accordance with the report; have the hand-held direct readout chlorine analyzer calibrated by a third party to confirm that it is reading accurately or to obtain a new hand-held unit to ensure accurate readings; ensure that all persons collecting water samples from the drinking water system have reviewed the owner's manual for the chlorine testing equipment being used and are obtaining test results in accordance with the users manual; submit records of daily treated chlorine residuals for two months; provide bottled water to the tenants of the site until it was determined that all treatment equipment met the requirements of Ontario Regulation 170/03 and was being maintained. | Provincial Officer's Order | Amended | No | 2022-08-04 | 2022-2023
Wainfleet | 260023595 | NMYRRS | Southlands Mobile Home Court Well Supply | 2390364 Ontario Inc O/A Albert Rumph | Wrc Purifying | This order required the owner of the drinking water system to retain a certified operator or an operating authority, provide proof of a written contract between the owner and the certified operator; and increase the frequency of distribution system microbiological sampling from bi-weekly to weekly. | Provincial Officer's Order | Issued | No | 2022-07-27 | 2022-2023
Smith-Ennismore-Lakefield | 260074035 | NMYRRS | 949 Sharon Court Well Supply | 2614722 Ontario Inc | Mcleods Eco Water | This order required the owner of the drinking water system to service and repair the UV disinfection system and the solenoid valve and ensure all treatment equipment is in proper working order; remove the bypass plumbing around the solenoid valve; and develop a standard operating procedure to ensure that the reporting requirements in Schedule 16 of O. Reg. 170/03 are met. | Provincial Officer's Order | Issued | No | 2022-10-13 | 2022-2023
Trent Hills | 260070863 | NMYRRS | Valleyview Retirement Estates Well Supply | Valleyview Resort | Kyle Coburn | This order required the owner of the drinking water system to ensure the well is properly fitted with a vermin proof well cap and submit photos of the completed work to the provincial officer; and the submission of maintenance, operational and sampling records to the provincial officer for the following four months. | Provincial Officer's Order | Issued | No | 2022-06-09 | 2022-2023
Kawartha Lakes | 260074230 | SNMNRS | Country Estates Retirement Home Cistern System | Country Estates Retirement Home Inc. | Country Estates Retirement Home Inc. | This order required the owner of the drinking water system to undertake visual inspections of the cistern, log the findings and report any findings that may indicate the cistern is failing or contamination has occurred until a new cistern has been installed; collect treated weekly microbiological samples until a new cistern has been installed; retain the services of a qualified person to complete the installation of a new cistern and provide proof of retention; provide a timeline and date of completion for the installation of the new cistern; and provide written confirmation that the installation of the new cistern is complete, and that the old cistern has been disconnected from the drinking water system. | Director's Order | Issued | Yes | 2022-12-09 | 2022-2023
Thunder Bay City | 220006197 | NMYRRS | Armstrong Well Supply | Armstrong Local Services Board | Clearford Waterworks Inc | This order required that the owner of the drinking water system provide weekly summary reports of system operations including sampling reports, operational, maintenance and alarm records; retain a certified operator to operate the drinking water system along with proof of a written contract between the owner and the certified operator; and to develop a contingency plan that includes procedures to ensure the site is operated by a certified operator. | Provincial Officer's Order | Amended | No | 2023-03-03 | 2022-2023